| # Case summary Cold-store temperature alarm repeating overnight | Case number: 00001030. Opened: 4 October 2026. Status: Working. Priority: High. |
| --- | --- |

Priority update commitment Updates will be provided every working day until this case is resolved.

| ## Customer Account Pellmore Foods Ltd Contact Tomás Ferreira Engineering Manager t.ferreira@pellmorefoods.example +44 117 555 0388 | ## Case details Type: Problem. Reason: Performance. Case Origin: Phone. Case Owner: Priya Desai. |
| --- | --- |

## Description

The monitoring unit on cold store 2 has raised a high-temperature alarm four times overnight. Store temperature logs stay within limits, so the sensor or its wiring is suspected. Stock has been moved to cold store 1 as a precaution.

## Current status

Open and being worked on.

## Updates

### Published comments

4 October 2026 15:49 — Priya Desai Replacement sensor and cable guard fitted this afternoon and calibrated against the reference probe (within 0.3 °C). We will watch the overnight trend before closing the case; stock can move back to cold store 2 tomorrow morning.

4 October 2026 15:16 — Priya Desai Engineer on site. Sensor T2-3 reads 6 °C warmer than a calibrated probe placed beside it, and its cable has chafed where it passes the evaporator door frame. We have fitted a temporary sensor so the alarm stays live, and ordered a replacement sensor and cable guard.

4 October 2026 13:30 — Priya Desai Thanks for the call this morning. The four alarms all came from sensor T2-3 between 01:40 and 04:10, while the two other sensors in cold store 2 held at -21 °C. That points to the sensor or its cable rather than the store itself. An engineer will attend today.

## Contact us

Please contact sales@forgeflow.example and quote case 00001030.