| # Field Service Report Annual inspection — 100 kW rooftop solar | Work order; 00000019. Visit date; 29 September 2026. Engineer; Priya Desai. Priority; Medium. Status; Completed. |
| --- | --- |

| ## Site details Coldharbour Leisure Centre 2 Coldharbour Road Swindon. | ## Customer contact Daniel Price d.price@coldharbourleisure.example +44 1793 555 410. |
| --- | --- |

| ## Technician Priya Desai Employer: HelioGrid. | ## Service timing Start: 29 September 2026 09:00 End: 29 September 2026 13:30. |
| --- | --- |

## Service checklist

☑ Work completed      ☑ Follow-up raised      ☑ Parts recorded      ☑ Labour recorded

## Assets inspected

| Asset | Finding | Outcome |
| --- | --- | --- |
| East roof array (124 modules) ARR-E-0124 | Follow-up: soiling on rows 3 to 5; cleaning booked | Follow-up |
| Inverter A (east roof) HG-INV-50K-21187 | Pass | Pass |
| Inverter B (west roof) HG-INV-50K-21188 | Pass | Pass |
| Monitoring gateway HG-GW-7731 | Pass · firmware updated to 4.2 | Pass |
| West roof array (118 modules) ARR-W-0118 | Pass | Pass |

## Recommended actions

| Action | Priority | Target date | Details |
| --- | --- | --- | --- |
| Clean east roof array, rows 3 to 5 | Medium | 13 October 2026 | Soft-brush and deionised water clean, then compare string yields with the west array. |

## Parts used

| Qty | Part | Notes |
| --- | --- | --- |
| 4 | DC string fuse 15 A | Replaced two blown string fuses and two spares |

## Labour

| Work carried out | Minutes |
| --- | --- |
| Inspection and testing | 195 min |
| Thermal imaging survey | 60 min |
| Report and handover | 15 min |

| ## Inspection outcomes | ## Time on site |
| --- | --- |

## Service summary

Annual inspection of both inverters, the east and west arrays and the monitoring gateway. Thermal imaging of the arrays, string testing and a firmware check on the inverters. One soiled section on the east array is booked for cleaning.

- Assets inspected: 5

- Part lines recorded: 1

- Time on site: 270 minutes

- Follow-up actions raised: 1

- Next planned visit: 28 September 2027

Service status: Completed

## Sign-off

|  | Engineer | Customer |
| --- | --- | --- |
| Signature |  |  |
| Name | Priya Desai |  |
| Date |  |  |

## Site photos